Manufacturer:

GDUK Door Solutions,

Securiparc House,

Wimsey Way,

Alfreton,

Derbyshire,

DE55 4LS.

Tel: 0800 316 6994.

Estimating: estimating@gdukds.com

Web: www.gdukds.com

FD20 Automatic Operator:

Gilgen electromechanical swing door operator with spring force close and adjustable closing EN 3-7, for different widths of door leaves in accordance with EN 1154.

Fully automatic or low energy operation complete with back check and adjustable hold open, transom mounted with standard rods/sliding rods fitted to door leaf.

Integrated INVERSE function- If required, the FD 20 can be configured to ‘Inverse’, in order for the door to always fail in the OPEN condition. This is especially suitable for smoke ventilation or emergency escapes.

Operator height 95mm, depth (back to front) 120mm, width 690mm.

Wind load regulation and integrated LCD control panel.

Maximum door leaf weight of 250kg.

Maximum leaf width 1600mm. Minimum door width 720mm.

Activation and control system per door set:

Built in program selector keys located on the side of the operator.

Key switch configured for off, automatic and hold open operating modes.

Entry

Activation sensor (delete as appropriate)

Stainless Steel Push Plate - engraved "Push to Open" (delete as appropriate)

Access control system (delete as appropriate)

Exit

Activation sensor (delete as appropriate)

Stainless Steel Push Plate engraved “Push to Open” (delete as appropriate)

Access control system (delete as appropriate)

Safety devices: (Each door leaf)

- 4Safe Infra-red safety sensors mounted on top rails of door leaves back and front to provide maximum safety. Complies with EN 16005.

- Flat Scan 3G Infra-red safety sensors mounted on top rails of door leaves back and front to provide maximum safety. Complies with EN 16005.

- Provision should also be made to protect against the potential hazards caused at the hinge or pivot stile – a suitable finger protection must be fitted to comply with EN16005 & the Machinery Directive 2006/42/EC.

Door Locks:

- Maglock (delete as appropriate)

- Electric strike (delete as appropriate)

- Manual centre lock (delete as appropriate)

Finishes:

- All visible operator surfaces to be Powder Coated to a standard RAL colour.

Signs:

- Standard signage to EN16005.

- Manifestation not included.

Other Requirements per door set:

- Standard covers.

- Continuous cover available for double door configurations

Barriers:

- Safety Barrier Rail- EN16005 – Barrier rails needed if side approach to doors is possible           (delete as appropriate)

- Not required. (delete as appropriate)

Associated works per door set:

- 1no. 240v 13A LIVE neon lit fused spur supply, protected by a 30mA RCD must be provided prior to installation. In compliance with BS EN16005 the mains connection must be capable of disconnection to safeguard against unintentional and unauthorised reactivation. Positioned above operator by others.

- Connection to the fire alarm system (if required) would require one pair of normally open volt free contacts to be supplied terminating at drive unit location by others.

- Any concealed containment (inc. draw wires) must be undertaken by others. Cabling to activation devices will otherwise be fitted with surface mini trunking at a minimum distance to suit industry standards.

- Installation carried out by the manufacturer’s engineers.  Installed to and complying with EN16005